# Proposed Rulemaking Report

10 CSR 23-3.030 Standards for Construction of Water Wells

Pursuant to Section 536.016, RSMo., an agency shall promulgate rules based upon substantial evidence on record. The following information identifies the necessity for the Missouri Department of Natural Resources to propose this rulemaking.

- What is the purpose of the rulemaking and why is it necessary?

The purpose of this rulemaking is to correctly incorporate by reference certain ASTM standards, improve rule clarity, correct erroneous data in Table 3.5, and add flexibilities to water well construction requirements. These changes are necessary to properly incorporate reference material pursuant to Chapter 536, RSMo, to ensure clarity, and to remove unnecessary restrictions related to drilling materials.

- What does the rulemaking require and how does it produce benefits?

This rulemaking requires that: 1) when geologic conditions require the use of telescoping casing, each succeeding smaller diameter of casing be extended into the preceding casing at least twenty feet; 2) boreholes for multi-family and high-yield wells be a minimum of four inches greater than the casing; 3) When plastic casing is used in lieu of steel for the construction of multi-family wells, the plastic casing shall be SCH 80 or SDR 17; and 4) public water supply wells must be constructed in accordance with rules and/or specifications outlined in 10 CSR 60-3. These requirements are already in PDWB rules. The new requirements produce benefits to by improving rule clarity and by adding flexibility to well construction material.

- Who has or will be involved in the development of the rulemaking?

Department of Natural Resources staff, Well Installation Board, stakeholders (well drillers and well owners), and citizens of Missouri.

- Who may I contact to either ask questions or provide input on this rulemaking?

Tiffany Wysong at 573 368-2196, Michelle Oglesby at 573 368-2115, in writing at P.O. Box 250, Rolla, MO 65402, or via email at tiffany.wysong@dnr.mo.gov and michelle.ogelsby@dnr.mo.gov

- What is the tentative schedule for this rulemaking (in particular the comment period and public hearing)?

We anticipate completion of draft rule language and rulemaking report October 14, 2022, program review February 1, 2023, Division request to begin rulemaking March 1, 2023, stakeholder meetings complete by May 1, 2023, public notice, comment period, and hearing fall 2023, rule effective spring 2024.